## June 2016
c2..p38
M:\OpenData\Data to upload\Uploaded (Week of 8.19.16)\DEP\[Monthly_Operating_Efficiency.xlsx]June 2016 | MONTHLY OPERATING EFFICIENCY
16 | CITY-WIDE BUBBLE
)\
| June | FLOW |  |  | TOTAL SUSPENDED SOLIDS | [7 empty] | CARBONACEOUS BIOCHEMICAL OXYGEN DEMAND
| 2016 | (MGD) |  |  | INFL |  | EFFLUENT (mg/L) |  |  | % REMOVAL |  |  | INFL |  | EFFLUENT (mg/L) |  |  | % REMOVAL
| PLANT | ACTUAL | 12-M RA | PERMIT | (mg/L) |  | ACTUAL |  | PERMIT | ACTUAL |  | PERMIT | (mg/L) |  | ACTUAL |  | PERMIT | ACTUAL |  | PERMIT
| WARDS ISLAND | 203 | 200 | 275 |  | 119 |  | 5 | 30 |  | 96% | 85% |  | 111 |  | 4 | 25 |  | 96% | 85%
| NORTH RIVER | 110 | 111 | 170 |  | 162 |  | 6 | 30 |  | 96% | 85% |  | 159 |  | 6 | 25 |  | 96% | 85%
| HUNTS POINT | 115 | 123 | 200 |  | 107 |  | 4 | 30 |  | 96% | 85% |  | 116 |  | 3 | 25 |  | 98% | 85%
| 26TH WARD | 44 | 44 | 85 |  | 113 |  | 6 | 30 |  | 95% | 85% |  | 143 |  | 4 | 25 |  | 97% | 85%
| CONEY ISLAND | 82 | 86 | 110 |  | 166 |  | 6 | 30 |  | 96% | 85% |  | 184 |  | 6 | 25 |  | 97% | 85%
| OWLS HEAD | 90 | 92 | 120 |  | 145 |  | 16 | 30 |  | 89% | 85% |  | 192 |  | 16 | 25 |  | 92% | 85%
| NEWTOWN CREEK | 204 | 209 | 310 |  | 180 |  | 10 | 30 |  | 94% | 85% |  | 182 |  | 12 | 25 |  | 93% | 85%
| RED HOOK | 25 | 26 | 60 |  | 178 |  | 4 | 30 |  | 98% | 85% |  | 180 |  | 4 | 25 |  | 98% | 85%
| JAMAICA | 76 | 76 | 100 |  | 161 |  | 9 | 30 |  | 94% | 85% |  | 197 |  | 7 | 25 |  | 96% | 85%
| TALLMAN ISLAND | 53 | 55.0833 | 80 |  | 138 |  | 7 | 30 |  | 95% | 85% |  | 144 |  | 7 | 25 |  | 95% | 85%
| BOWERY BAY | 93 | 100 | 150 |  | 152 |  | 4 | 30 |  | 98% | 85% |  | 162 |  | 3 | 25 |  | 98% | 85%
| ROCKAWAY | 17 | 16 | 45 |  | 95 |  | 6 | 30 |  | 94% | 85% |  | 124 |  | 4 | 25 |  | 97% | 85%
| OAKWOOD BEACH | 25.4 | 25.7 | 39.9 |  | 353 |  | 10 | 30 |  | 97% | 85% |  | 280 |  | 9 | 25 |  | 97% | 85%
| PORT RICHMOND | 24 | 26 | 60 |  | 364 |  | 6 | 30 |  | 98% | 85% |  | 431 |  | 7 | 25 |  | 98% | 85%
| TOTAL | 1161 | 1190 | 1804.9
| Weighted Average |  |  |  |  | 155.1156 |  | 7.2334 |  |  | 95% |  |  | 164.4143 |  | 6.9936 |  |  | 96% | 85%
|  | 12- Month Running Averages: | [7 empty] | 94.17% |  | 85% |  | #REF! |  | #REF! |  |  | 95.33% | 85%
NOTES:
| (1) | All weighted averages based on Total Flow.
| (2) | System-Wide (weighted average) limit for TSS and CBOD % Removals: 85%; and a 12-month running avg. of 85%.
| (3) | Permit flows are for 12-month rolling averages of the total flows.

## May 2016
MONTHLY OPERATING EFFICIENCY
CITY-WIDE BUBBLE
May | FLOW |  |  | TOTAL SUSPENDED SOLIDS | [7 empty] | CARBONACEOUS BIOCHEMICAL OXYGEN DEMAND
2016 | (MGD) |  |  | INFL |  | EFFLUENT (mg/L) |  |  | % REMOVAL |  |  | INFL |  | EFFLUENT (mg/L) |  |  | % REMOVAL
PLANT | ACTUAL | 12-M RA | PERMIT | (mg/L) |  | ACTUAL |  | PERMIT | ACTUAL |  | PERMIT | (mg/L) |  | ACTUAL |  | PERMIT | ACTUAL |  | PERMIT
WARDS ISLAND | 198 | 201 | 275 |  | 132 |  | 17 | 30 |  | 87% | 85% |  | 113 |  | 6 | 25 |  | 95% | 85%
NORTH RIVER | 108 | 112 | 170 |  | 166 |  | 10 | 30 |  | 94% | 85% |  | 151 |  | 6 | 25 |  | 96% | 85%
HUNTS POINT | 122 | 123 | 200 |  | 109 |  | 5 | 30 |  | 95% | 85% |  | 112 |  | 2 | 25 |  | 98% | 85%
26TH WARD | 48 | 44 | 85 |  | 112 |  | 5 | 30 |  | 96% | 85% |  | 147 |  | 5 | 25 |  | 97% | 85%
CONEY ISLAND | 89 | 87 | 110 |  | 183 |  | 9 | 30 |  | 96% | 85% |  | 184 |  | 8 | 25 |  | 96% | 85%
OWLS HEAD | 96 | 93 | 120 |  | 142 |  | 11 | 30 |  | 93% | 85% |  | 202 |  | 12 | 25 |  | 95% | 85%
NEWTOWN CREEK | 202 | 211 | 310 |  | 176 |  | 9 | 30 |  | 95% | 85% |  | 190 |  | 12 | 25 |  | 94% | 85%
RED HOOK | 26 | 26 | 60 |  | 243 |  | 8 | 30 |  | 97% | 85% |  | 221 |  | 9 | 25 |  | 96% | 85%
JAMAICA | 77 | 76 | 100 |  | 150 |  | 12 | 30 |  | 92% | 85% |  | 194 |  | 9 | 25 |  | 95% | 85%
TALLMAN ISLAND | 56 | 56.0833 | 80 |  | 143 |  | 10 | 30 |  | 94% | 85% |  | 139 |  | 8 | 25 |  | 94% | 85%
BOWERY BAY | 97 | 102 | 150 |  | 166 |  | 7 | 30 |  | 96% | 85% |  | 161 |  | 4 | 25 |  | 98% | 85%
ROCKAWAY | 16 | 16 | 45 |  | 96 |  | 4 | 30 |  | 96% | 85% |  | 125 |  | 3 | 25 |  | 98% | 85%
OAKWOOD BEACH | 27.2 | 26 | 39.9 |  | 247 |  | 5 | 30 |  | 98% | 85% |  | 211 |  | 7 | 25 |  | 97% | 85%
PORT RICHMOND | 25 | 26 | 60 |  | 204 |  | 4 | 30 |  | 98% | 85% |  | 310 |  | 6 | 25 |  | 98% | 85%
TOTAL | 1187 | 1199 | 1804.9
Weighted Average |  |  |  |  | 154.6263 |  | 9.8079 |  |  | 94% |  |  | 162.6994 |  | 7.3794 |  |  | 95% | 85%
| 12- Month Running Averages: | [7 empty] | 93.6% |  | 85% |  | #REF! |  | #REF! |  |  | 94.8% | 85%
NOTES:
(1) | All weighted averages based on Total Flow.
(2) | System-Wide (weighted average) limit for TSS and CBOD % Removals: 85%; and a 12-month running avg. of 85%.
(3) | Permit flows are for 12-month rolling averages of the total flows.

## April 2016
MONTHLY OPERATING EFFICIENCY
CITY-WIDE BUBBLE
April | FLOW |  |  | TOTAL SUSPENDED SOLIDS | [7 empty] | CARBONACEOUS BIOCHEMICAL OXYGEN DEMAND
2016 | (MGD) |  |  | INFL |  | EFFLUENT (mg/L) |  |  | % REMOVAL |  |  | INFL |  | EFFLUENT (mg/L) |  |  | % REMOVAL
PLANT | ACTUAL | 12-M RA | PERMIT | (mg/L) |  | ACTUAL |  | PERMIT | ACTUAL |  | PERMIT | (mg/L) |  | ACTUAL |  | PERMIT | ACTUAL |  | PERMIT
WARDS ISLAND | 188 | 201 | 275 |  | 133 |  | 16 | 30 |  | 88% | 85% |  | 109 |  | 6 | 25 |  | 94% | 85%
NORTH RIVER | 103 | 112 | 170 |  | 168 |  | 9 | 30 |  | 95% | 85% |  | 155 |  | 6 | 25 |  | 96% | 85%
HUNTS POINT | 116 | 122 | 200 |  | 117 |  | 5 | 30 |  | 96% | 85% |  | 107 |  | 3 | 25 |  | 97% | 85%
26TH WARD | 45 | 44 | 85 |  | 124 |  | 4 | 30 |  | 97% | 85% |  | 153 |  | 4 | 25 |  | 97% | 85%
CONEY ISLAND | 82 | 86 | 110 |  | 200 |  | 14 | 30 |  | 93% | 85% |  | 194 |  | 9 | 25 |  | 95% | 85%
OWLS HEAD | 88 | 92 | 120 |  | 170 |  | 18 | 30 |  | 89% | 85% |  | 240 |  | 16 | 25 |  | 93% | 85%
NEWTOWN CREEK | 196 | 210 | 310 |  | 173 |  | 13 | 30 |  | 92% | 85% |  | 182 |  | 12 | 25 |  | 93% | 85%
RED HOOK | 24 | 26 | 60 |  | 353 |  | 4 | 30 |  | 99% | 85% |  | 231 |  | 4 | 25 |  | 98% | 85%
JAMAICA | 74 | 76 | 100 |  | 155 |  | 14 | 30 |  | 91% | 85% |  | 198 |  | 10 | 25 |  | 95% | 85%
TALLMAN ISLAND | 51 | 55.5833 | 80 |  | 147 |  | 10 | 30 |  | 93% | 85% |  | 135 |  | 5 | 25 |  | 96% | 85%
BOWERY BAY | 91 | 102 | 150 |  | 161 |  | 7 | 30 |  | 96% | 85% |  | 151 |  | 4 | 25 |  | 97% | 85%
ROCKAWAY | 14 | 16 | 45 |  | 96 |  | 3 | 30 |  | 97% | 85% |  | 140 |  | 4 | 25 |  | 97% | 85%
OAKWOOD BEACH | 24.4 | 25.7 | 39.9 |  | 249 |  | 4 | 30 |  | 98% | 85% |  | 214 |  | 7 | 25 |  | 97% | 85%
PORT RICHMOND | 24 | 27 | 60 |  | 218 |  | 4 | 30 |  | 98% | 85% |  | 349 |  | 6 | 25 |  | 98% | 85%
TOTAL | 1120 | 1195 | 1804.9
Weighted Average |  |  |  |  | 162.0264 |  | 11.1514 |  |  | 93% |  |  | 165.03 |  | 7.6766 |  |  | 95% | 85%
| 12- Month Running Averages: | [7 empty] | 93% |  | 85% |  | #REF! |  | #REF! |  |  | 94.75% | 85%
NOTES:
(1) | All weighted averages based on Total Flow.
(2) | System-Wide (weighted average) limit for TSS and CBOD % Removals: 85%; and a 12-month running avg. of 85%.
(3) | Permit flows are for 12-month rolling averages of the total flows.

## March 2016
MONTHLY OPERATING EFFICIENCY
CITY-WIDE BUBBLE
2016-03-01 | FLOW |  |  | TOTAL SUSPENDED SOLIDS | [7 empty] | CARBONACEOUS BIOCHEMICAL OXYGEN DEMAND
2016 | (MGD) |  |  | INFL |  | EFFLUENT (mg/L) |  |  | % REMOVAL |  |  | INFL |  | EFFLUENT (mg/L) |  |  | % REMOVAL
PLANT | ACTUAL | 12-M RA | PERMIT | (mg/L) |  | ACTUAL |  | PERMIT | ACTUAL |  | PERMIT | (mg/L) |  | ACTUAL |  | PERMIT | ACTUAL |  | PERMIT
WARDS ISLAND | 185 | 203 | 275 |  | 140 |  | 8 | 30 |  | 94% | 85% |  | 112 |  | 3 | 25 |  | 97% | 85%
NORTH RIVER | 103 | 113 | 170 |  | 179 |  | 10 | 30 |  | 94% | 85% |  | 150 |  | 7 | 25 |  | 95% | 85%
HUNTS POINT | 116 | 122 | 200 |  | 120 |  | 4 | 30 |  | 97% | 85% |  | 106 |  | 2 | 25 |  | 98% | 85%
26TH WARD | 39 | 43 | 85 |  | 108 |  | 9 | 30 |  | 92% | 85% |  | 150 |  | 5 | 25 |  | 97% | 85%
CONEY ISLAND | 82 | 85 | 110 |  | 160 |  | 12 | 30 |  | 92% | 85% |  | 189 |  | 7 | 25 |  | 96% | 85%
OWLS HEAD | 88 | 92 | 120 |  | 153 |  | 16 | 30 |  | 90% | 85% |  | 234 |  | 14 | 25 |  | 94% | 85%
NEWTOWN CREEK | 199 | 211 | 310 |  | 171 |  | 12 | 30 |  | 93% | 85% |  | 185 |  | 11 | 25 |  | 94% | 85%
RED HOOK | 25 | 26 | 60 |  | 335 |  | 7 | 30 |  | 98% | 85% |  | 245 |  | 6 | 25 |  | 98% | 85%
JAMAICA | 75 | 76 | 100 |  | 157 |  | 9 | 30 |  | 94% | 85% |  | 200 |  | 7 | 25 |  | 97% | 85%
TALLMAN ISLAND | 51 | 55.75 | 80 |  | 151 |  | 5 | 30 |  | 97% | 85% |  | 130 |  | 4 | 25 |  | 97% | 85%
BOWERY BAY | 91 | 103 | 150 |  | 149 |  | 12 | 30 |  | 92% | 85% |  | 144 |  | 6 | 25 |  | 96% | 85%
ROCKAWAY | 15 | 16 | 45 |  | 100 |  | 5 | 30 |  | 95% | 85% |  | 133 |  | 4 | 25 |  | 97% | 85%
OAKWOOD BEACH | 25.8 | 26 | 39.9 |  | 183 |  | 6 | 30 |  | 97% | 85% |  | 178 |  | 7 | 25 |  | 96% | 85%
PORT RICHMOND | 27 | 27 | 60 |  | 177 |  | 6 | 30 |  | 97% | 85% |  | 330 |  | 7 | 25 |  | 98% | 85%
TOTAL | 1122 | 1199 | 1804.9
Weighted Average |  |  |  |  | 156.4103 |  | 9.531 |  |  | 94% |  |  | 163.6162 |  | 6.7314 |  |  | 96% | 85%
| 12- Month Running Averages: | [7 empty] | 93.67% |  | 85% |  | #REF! |  | #VALUE! |  |  | 95.33% | 85%
NOTES:
(1) | All weighted averages based on Total Flow.
(2) | System-Wide (weighted average) limit for TSS and CBOD % Removals: 85%; and a 12-month running avg. of 85%.
(3) | Permit flows are for 12-month rolling averages of the total flows.
196
233
274
289
302
304
300
299
300
296
284
281
281
281
276
272
274
265
241
226
211
197
189
188
260.7917

## February 2016
MONTHLY OPERATING EFFICIENCY
CITY-WIDE BUBBLE
February | FLOW |  |  | TOTAL SUSPENDED SOLIDS | [7 empty] | CARBONACEOUS BIOCHEMICAL OXYGEN DEMAND
2016 | (MGD) |  |  | INFL |  | EFFLUENT (mg/L) |  |  | % REMOVAL |  |  | INFL |  | EFFLUENT (mg/L) |  |  | % REMOVAL
PLANT | ACTUAL | 12-M RA | PERMIT | (mg/L) |  | ACTUAL |  | PERMIT | ACTUAL |  | PERMIT | (mg/L) |  | ACTUAL |  | PERMIT | ACTUAL |  | PERMIT
WARDS ISLAND | 205 | 206 | 275 |  | 123 |  | 12 | 30 |  | 92% | 85% |  | 100 |  | 5 | 25 |  | 96% | 85%
NORTH RIVER | 117 | 114 | 170 |  | 167 |  | 22 | 30 |  | 87% | 85% |  | 134 |  | 10 | 25 |  | 93% | 85%
HUNTS POINT | 139 | 125 | 200 |  | 109 |  | 7 | 30 |  | 95% | 85% |  | 88 |  | 3 | 25 |  | 98% | 85%
26TH WARD | 51 | 44 | 85 |  | 113 |  | 8 | 30 |  | 94% | 85% |  | 142 |  | 5 | 25 |  | 97% | 85%
CONEY ISLAND | 94 | 86 | 110 |  | 141 |  | 28 | 30 |  | 81% | 85% |  | 154 |  | 19 | 25 |  | 88% | 85%
OWLS HEAD | 103 | 93 | 120 |  | 137 |  | 24 | 30 |  | 86% | 85% |  | 192 |  | 17 | 25 |  | 93% | 85%
NEWTOWN CREEK | 223 | 213 | 310 |  | 171 |  | 11 | 30 |  | 93% | 85% |  | 157 |  | 11 | 25 |  | 93% | 85%
RED HOOK | 29 | 26 | 60 |  | 216 |  | 8 | 30 |  | 97% | 85% |  | 197 |  | 7 | 25 |  | 97% | 85%
JAMAICA | 81 | 77 | 100 |  | 138 |  | 12 | 30 |  | 91% | 85% |  | 184 |  | 8 | 25 |  | 96% | 85%
TALLMAN ISLAND | 64 | 57.25 | 80 |  | 127 |  | 9 | 30 |  | 94% | 85% |  | 114 |  | 4 | 25 |  | 97% | 85%
BOWERY BAY | 112 | 106 | 150 |  | 125 |  | 14 | 30 |  | 90% | 85% |  | 121 |  | 7 | 25 |  | 95% | 85%
ROCKAWAY | 16 | 16 | 45 |  | 95 |  | 4 | 30 |  | 96% | 85% |  | 108 |  | 3 | 25 |  | 97% | 85%
OAKWOOD BEACH | 30.6 | 26.7 | 39.9 |  | 119 |  | 13 | 30 |  | 90% | 85% |  | 148 |  | 10 | 25 |  | 94% | 85%
PORT RICHMOND | 35 | 28 | 60 |  | 167 |  | 19 | 30 |  | 90% | 85% |  | 280 |  | 14 | 25 |  | 96% | 85%
TOTAL | 1300 | 1218 | 1804.9
Weighted Average |  |  |  |  | 139.8018 |  | 14.1898 |  |  | 90% |  |  | 140.336 |  | 8.9169 |  |  | 94% | 85%
| 12- Month Running Averages: | [7 empty] | 90% |  | 85% |  | #REF! |  | #VALUE! |  |  | 94% | 85%
NOTES:
(1) | All weighted averages based on Total Flow.
(2) | System-Wide (weighted average) limit for TSS and CBOD % Removals: 85%; and a 12-month running avg. of 85%.
(3) | Permit flows are for 12-month rolling averages of the total flows.
196
233
274
289
302
304
300
299
300
296
284
281
281
281
276
272
274
265
241
226
211
197
189
188
260.7917

## January 2016
MONTHLY OPERATING EFFICIENCY
CITY-WIDE BUBBLE
January | FLOW |  |  | TOTAL SUSPENDED SOLIDS | [7 empty] | CARBONACEOUS BIOCHEMICAL OXYGEN DEMAND
2016 | (MGD) |  |  | INFL |  | EFFLUENT (mg/L) |  |  | % REMOVAL |  |  | INFL |  | EFFLUENT (mg/L) |  |  | % REMOVAL
PLANT | ACTUAL | 12-M RA | PERMIT | (mg/L) |  | ACTUAL |  | PERMIT | ACTUAL |  | PERMIT | (mg/L) |  | ACTUAL |  | PERMIT | ACTUAL |  | PERMIT
WARDS ISLAND | 190 | 205 | 275 |  | 136 |  | 8 | 30 |  | 95% | 85% |  | 112 |  | 3 | 25 |  | 97% | 85%
NORTH RIVER | 113 | 114 | 170 |  | 152 |  | 8 | 30 |  | 95% | 85% |  | 139 |  | 5 | 25 |  | 96% | 85%
HUNTS POINT | 122 | 123 | 200 |  | 112 |  | 8 | 30 |  | 94% | 85% |  | 102 |  | 3 | 25 |  | 97% | 85%
26TH WARD | 44 | 43 | 85 |  | 102 |  | 5 | 30 |  | 95% | 85% |  | 145 |  | 5 | 25 |  | 97% | 85%
CONEY ISLAND | 88 | 86 | 110 |  | 147 |  | 17 | 30 |  | 89% | 85% |  | 156 |  | 31 | 25 |  | 81% | 85%
OWLS HEAD | 92 | 92 | 120 |  | 142 |  | 13 | 30 |  | 91% | 85% |  | 199 |  | 12 | 25 |  | 94% | 85%
NEWTOWN CREEK | 210 | 212 | 310 |  | 147 |  | 9 | 30 |  | 94% | 85% |  | 163 |  | 11 | 25 |  | 93% | 85%
RED HOOK | 26 | 26 | 60 |  | 158 |  | 5 | 30 |  | 97% | 85% |  | 183 |  | 7 | 25 |  | 96% | 85%
JAMAICA | 74 | 77 | 100 |  | 135 |  | 12 | 30 |  | 91% | 85% |  | 194 |  | 8 | 25 |  | 96% | 85%
TALLMAN ISLAND | 54 | 56.4167 | 80 |  | 131 |  | 13 | 30 |  | 90% | 85% |  | 128 |  | 6 | 25 |  | 95% | 85%
BOWERY BAY | 103 | 105 | 150 |  | 139 |  | 16 | 30 |  | 89% | 85% |  | 140 |  | 7 | 25 |  | 95% | 85%
ROCKAWAY | 16 | 16 | 45 |  | 101 |  | 5 | 30 |  | 95% | 85% |  | 114 |  | 3 | 25 |  | 97% | 85%
OAKWOOD BEACH | 26.7 | 26.4 | 39.9 |  | 184 |  | 8 | 30 |  | 96% | 85% |  | 180 |  | 10 | 25 |  | 95% | 85%
PORT RICHMOND | 28 | 27 | 60 |  | 201 |  | 13 | 30 |  | 94% | 85% |  | 331 |  | 12 | 25 |  | 96% | 85%
TOTAL | 1187 | 1209 | 1804.9
Weighted Average |  |  |  |  | 139.582 |  | 10.3013 |  |  | 93% |  |  | 150.3126 |  | 8.7051 |  |  | 94% | 85%
| 12- Month Running Averages: | [7 empty] | 93% |  | 85% |  | #REF! |  | #REF! |  |  | 94% | 85%
NOTES:
(1) | All weighted averages based on Total Flow.
(2) | System-Wide (weighted average) limit for TSS and CBOD % Removals: 85%; and a 12-month running avg. of 85%.
(3) | Permit flows are for 12-month rolling averages of the total flows.
196
233
274
289
302
304
300
299
300
296
284
281
281
281
276
272
274
265
241
226
211
197
189
188
260.7917

## January 2015
MONTHLY OPERATING EFFICIENCY
CITY-WIDE BUBBLE
January | FLOW |  |  | TOTAL SUSPENDED SOLIDS | [7 empty] | CARBONACEOUS BIOCHEMICAL OXYGEN DEMAND
2015 | (MGD) |  |  | INFL |  | EFFLUENT (mg/L) |  |  | % REMOVAL |  |  | INFL |  | EFFLUENT (mg/L) |  |  | % REMOVAL
PLANT | ACTUAL | 12-M RA | PERMIT | (mg/L) |  | ACTUAL |  | PERMIT | ACTUAL |  | PERMIT | (mg/L) |  | ACTUAL |  | PERMIT | ACTUAL |  | PERMIT
WARDS ISLAND | 203 | 211 | 275 |  | 113 |  | 13 | 30 |  | 91% | 85% |  | 90 |  | 4 | 25 |  | 96% | 85%
NORTH RIVER | 115 | 116 | 170 |  | 161 |  | 23 | 30 |  | 87% | 85% |  | 123 |  | 11 | 25 |  | 91% | 85%
HUNTS POINT | 130 | 123 | 200 |  | 124 |  | 12 | 30 |  | 94% | 85% |  | 113 |  | 3 | 25 |  | 98% | 85%
26TH WARD | 44 | 47 | 85 |  | 94 |  | 16 | 30 |  | 88% | 85% |  | 135 |  | 6 | 25 |  | 96% | 85%
CONEY ISLAND | 91 | 88 | 110 |  | 235 |  | 13 | 30 |  | 94% | 85% |  | 165 |  | 7 | 25 |  | 96% | 85%
OWLS HEAD | 95 | 94 | 120 |  | 144 |  | 49 | 30 |  | 77% | 85% |  | 168 |  | 22 | 25 |  | 90% | 85%
NEWTOWN CREEK | 219 | 219 | 310 |  | 140 |  | 12 | 30 |  | 91% | 85% |  | 145 |  | 11 | 25 |  | 93% | 85%
RED HOOK | 28 | 28 | 60 |  | 155 |  | 5 | 30 |  | 97% | 85% |  | 167 |  | 6 | 25 |  | 96% | 85%
JAMAICA | 81 | 79 | 100 |  | 148 |  | 14 | 30 |  | 91% | 85% |  | 122 |  | 5 | 25 |  | 96% | 85%
TALLMAN ISLAND | 60 | 58.6667 | 80 |  | 123 |  | 11 | 30 |  | 93% | 85% |  | 100 |  | 5 | 25 |  | 96% | 85%
BOWERY BAY | 111 | 110 | 150 |  | 154 |  | 10 | 30 |  | 95% | 85% |  | 121 |  | 5 | 25 |  | 98% | 85%
ROCKAWAY | 15 | 16 | 45 |  | 89 |  | 7 | 30 |  | 92% | 85% |  | 101 |  | 4 | 25 |  | 96% | 85%
OAKWOOD BEACH | 30.2 | 29.6 | 39.9 |  | 155 |  | 8 | 30 |  | 95% | 85% |  | 138 |  | 6 | 25 |  | 96% | 85%
PORT RICHMOND | 32 | 31 | 60 |  | 147 |  | 7 | 30 |  | 96% | 85% |  | 240 |  | 6 | 25 |  | 98% | 85%
TOTAL | 1254 | 1250 | 1804.9
Weighted Average |  |  |  |  | 142.7089 |  | 15.6528 |  |  | 89% |  |  | 130.085 |  | 7.7577 |  |  | 94% | 85%
| 12- Month Running Averages: | [7 empty] | 91.75% |  | 85% |  | #REF! |  | #REF! |  |  | 94.5% | 85%
NOTES:
(1) | All weighted averages based on Total Flow.
(2) | System-Wide (weighted average) limit for TSS and CBOD % Removals: 85%; and a 12-month running avg. of 85%.
(3) | Permit flows are for 12-month rolling averages of the total flows.

## February 2015
MONTHLY OPERATING EFFICIENCY
CITY-WIDE BUBBLE
February | FLOW |  |  | TOTAL SUSPENDED SOLIDS | [7 empty] | CARBONACEOUS BIOCHEMICAL OXYGEN DEMAND
2015 | (MGD) |  |  | INFL |  | EFFLUENT (mg/L) |  |  | % REMOVAL |  |  | INFL |  | EFFLUENT (mg/L) |  |  | % REMOVAL
PLANT | ACTUAL | 12-M RA | PERMIT | (mg/L) |  | ACTUAL |  | PERMIT | ACTUAL |  | PERMIT | (mg/L) |  | ACTUAL |  | PERMIT | ACTUAL |  | PERMIT
WARDS ISLAND | 192 | 210 | 275 |  | 117 |  | 6 | 30 |  | 95% | 85% |  | 95 |  | 3 | 25 |  | 97% | 85%
NORTH RIVER | 111 | 116 | 170 |  | 156 |  | 9 | 30 |  | 94% | 85% |  | 122 |  | 6 | 25 |  | 95% | 85%
HUNTS POINT | 121 | 121 | 200 |  | 120 |  | 7 | 30 |  | 94% | 85% |  | 100 |  | 2 | 25 |  | 98% | 85%
26TH WARD | 42 | 47 | 85 |  | 95 |  | 7 | 30 |  | 93% | 85% |  | 133 |  | 7 | 25 |  | 95% | 85%
CONEY ISLAND | 84 | 87 | 110 |  | 165 |  | 18 | 30 |  | 89% | 85% |  | 140 |  | 11 | 25 |  | 92% | 85%
OWLS HEAD | 93 | 93 | 120 |  | 178 |  | 29 | 30 |  | 87% | 85% |  | 198 |  | 14 | 25 |  | 94% | 85%
NEWTOWN CREEK | 214 | 218 | 310 |  | 155 |  | 14 | 30 |  | 92% | 85% |  | 158 |  | 13 | 25 |  | 92% | 85%
RED HOOK | 25 | 28 | 60 |  | 159 |  | 6 | 30 |  | 96% | 85% |  | 189 |  | 7 | 25 |  | 96% | 85%
JAMAICA | 78 | 79 | 100 |  | 139 |  | 17 | 30 |  | 89% | 85% |  | 122 |  | 5 | 25 |  | 96% | 85%
TALLMAN ISLAND | 54 | 58.25 | 80 |  | 131 |  | 17 | 30 |  | 87% | 85% |  | 100 |  | 5 | 25 |  | 95% | 85%
BOWERY BAY | 105 | 109 | 150 |  | 157 |  | 7 | 30 |  | 96% | 85% |  | 134 |  | 3 | 25 |  | 98% | 85%
ROCKAWAY | 13 | 16 | 45 |  | 98 |  | 4 | 30 |  | 96% | 85% |  | 97 |  | 3 | 25 |  | 97% | 85%
OAKWOOD BEACH | 27.8 | 29.2 | 39.9 |  | 176 |  | 14 | 30 |  | 93% | 85% |  | 142 |  | 8 | 25 |  | 94% | 85%
PORT RICHMOND | 29 | 31 | 60 |  | 177 |  | 5 | 30 |  | 97% | 85% |  | 250 |  | 4 | 25 |  | 98% | 85%
TOTAL | 1189 | 1242 | 1804.9
Weighted Average |  |  |  |  | 144.2807 |  | 11.9531 |  |  | 92% |  |  | 134.2503 |  | 6.9919 |  |  | 95% | 85%
| 12- Month Running Averages: | [7 empty] | 91.92% |  | 85% |  | #REF! |  | #REF! |  |  | 94.67% | 85%
NOTES:
(1) | All weighted averages based on Total Flow.
(2) | System-Wide (weighted average) limit for TSS and CBOD % Removals: 85%; and a 12-month running avg. of 85%.
(3) | Permit flows are for 12-month rolling averages of the total flows.

## March 2015
MONTHLY OPERATING EFFICIENCY
CITY-WIDE BUBBLE
March | FLOW |  |  | TOTAL SUSPENDED SOLIDS | [7 empty] | CARBONACEOUS BIOCHEMICAL OXYGEN DEMAND
2015 | (MGD) |  |  | INFL |  | EFFLUENT (mg/L) |  |  | % REMOVAL |  |  | INFL |  | EFFLUENT (mg/L) |  |  | % REMOVAL
PLANT | ACTUAL | 12-M RA | PERMIT | (mg/L) |  | ACTUAL |  | PERMIT | ACTUAL |  | PERMIT | (mg/L) |  | ACTUAL |  | PERMIT | ACTUAL |  | PERMIT
WARDS ISLAND | 226 | 212 | 275 |  | 110 |  | 9 | 30 |  | 94% | 85% |  | 83 |  | 4 | 25 |  | 95% | 85%
NORTH RIVER | 122 | 117 | 170 |  | 172 |  | 19 | 30 |  | 90% | 85% |  | 123 |  | 9 | 25 |  | 93% | 85%
HUNTS POINT | 148 | 123 | 200 |  | 107 |  | 9 | 30 |  | 93% | 85% |  | 84 |  | 3 | 25 |  | 98% | 85%
26TH WARD | 48 | 47 | 85 |  | 121 |  | 12 | 30 |  | 93% | 85% |  | 132 |  | 7 | 25 |  | 96% | 85%
CONEY ISLAND | 95 | 88 | 110 |  | 156 |  | 25 | 30 |  | 84% | 85% |  | 147 |  | 37 | 25 |  | 75% | 85%
OWLS HEAD | 103 | 94 | 120 |  | 164 |  | 30 | 30 |  | 86% | 85% |  | 171 |  | 17 | 25 |  | 92% | 85%
NEWTOWN CREEK | 230 | 214 | 310 |  | 157 |  | 14 | 30 |  | 91% | 85% |  | 149 |  | 13 | 25 |  | 92% | 85%
RED HOOK | 29 | 28 | 60 |  | 170 |  | 6 | 30 |  | 96% | 85% |  | 168 |  | 6 | 25 |  | 96% | 85%
JAMAICA | 86 | 80 | 100 |  | 133 |  | 16 | 30 |  | 90% | 85% |  | 115 |  | 6 | 25 |  | 96% | 85%
TALLMAN ISLAND | 69 | 59.6667 | 80 |  | 121 |  | 11 | 30 |  | 93% | 85% |  | 88 |  | 5 | 25 |  | 96% | 85%
BOWERY BAY | 122 | 111 | 150 |  | 139 |  | 9 | 30 |  | 95% | 85% |  | 120 |  | 4 | 25 |  | 97% | 85%
ROCKAWAY | 14 | 16 | 45 |  | 97 |  | 6 | 30 |  | 94% | 85% |  | 108 |  | 3 | 25 |  | 97% | 85%
OAKWOOD BEACH | 34 | 29.5 | 39.9 |  | 128 |  | 11 | 30 |  | 91% | 85% |  | 134 |  | 8 | 25 |  | 94% | 85%
PORT RICHMOND | 38 | 31 | 60 |  | 140 |  | 6 | 30 |  | 96% | 85% |  | 220 |  | 5 | 25 |  | 98% | 85%
TOTAL | 1364 | 1250 | 1804.9
Weighted Average |  |  |  |  | 137.8409 |  | 13.9575 |  |  | 90% |  |  | 123.3739 |  | 9.5784 |  |  | 92% | 85%
| 12- Month Running Averages: | [7 empty] | 91.83% |  | 85% |  | #REF! |  | #REF! |  |  | 94.5% | 85%
NOTES:
(1) | All weighted averages based on Total Flow.
(2) | System-Wide (weighted average) limit for TSS and CBOD % Removals: 85%; and a 12-month running avg. of 85%.
(3) | Permit flows are for 12-month rolling averages of the total flows.

## April 2015
MONTHLY OPERATING EFFICIENCY
CITY-WIDE BUBBLE
April | FLOW |  |  | TOTAL SUSPENDED SOLIDS | [7 empty] | CARBONACEOUS BIOCHEMICAL OXYGEN DEMAND
2015 | (MGD) |  |  | INFL |  | EFFLUENT (mg/L) |  |  | % REMOVAL |  |  | INFL |  | EFFLUENT (mg/L) |  |  | % REMOVAL
PLANT | ACTUAL | 12-M RA | PERMIT | (mg/L) |  | ACTUAL |  | PERMIT | ACTUAL |  | PERMIT | (mg/L) |  | ACTUAL |  | PERMIT | ACTUAL |  | PERMIT
WARDS ISLAND | 201 | 211 | 275 |  | 117 |  | 6 | 30 |  | 96% | 85% |  | 91 |  | 4 | 25 |  | 96% | 85%
NORTH RIVER | 113 | 116 | 170 |  | 152 |  | 18 | 30 |  | 88% | 85% |  | 129 |  | 9 | 25 |  | 93% | 85%
HUNTS POINT | 117 | 121 | 200 |  | 126 |  | 5 | 30 |  | 96% | 85% |  | 100 |  | 2 | 25 |  | 98% | 85%
26TH WARD | 39 | 46 | 85 |  | 113 |  | 5 | 30 |  | 96% | 85% |  | 154 |  | 4 | 25 |  | 97% | 85%
CONEY ISLAND | 78 | 87 | 110 |  | 134 |  | 44 | 30 |  | 69% | 85% |  | 148 |  | 38 | 25 |  | 75% | 85%
OWLS HEAD | 88 | 94 | 120 |  | 177 |  | 14 | 30 |  | 93% | 85% |  | 197 |  | 8 | 25 |  | 96% | 85%
NEWTOWN CREEK | 201 | 218 | 310 |  | 168 |  | 14 | 30 |  | 92% | 85% |  | 179 |  | 14 | 25 |  | 92% | 85%
RED HOOK | 25 | 28 | 60 |  | 228 |  | 6 | 30 |  | 97% | 85% |  | 198 |  | 7 | 25 |  | 96% | 85%
JAMAICA | 78 | 80 | 100 |  | 156 |  | 8 | 30 |  | 95% | 85% |  | 189 |  | 6 | 25 |  | 97% | 85%
TALLMAN ISLAND | 53 | 59 | 80 |  | 141 |  | 9 | 30 |  | 94% | 85% |  | 116 |  | 4 | 25 |  | 97% | 85%
BOWERY BAY | 103 | 110 | 150 |  | 157 |  | 7 | 30 |  | 96% | 85% |  | 137 |  | 3 | 25 |  | 98% | 85%
ROCKAWAY | 14 | 16 | 45 |  | 102 |  | 4 | 30 |  | 96% | 85% |  | 118 |  | 2 | 25 |  | 98% | 85%
OAKWOOD BEACH | 27.3 | 29.1 | 39.9 |  | 164 |  | 14 | 30 |  | 91% | 85% |  | 155 |  | 10 | 25 |  | 94% | 85%
PORT RICHMOND | 27 | 31 | 60 |  | 185 |  | 26 | 30 |  | 86% | 85% |  | 273 |  | 14 | 25 |  | 95% | 85%
TOTAL | 1164 | 1246 | 1804.9
Weighted Average |  |  |  |  | 147.8095 |  | 12.5517 |  |  | 92% |  |  | 144.8784 |  | 9.0515 |  |  | 94% | 85%
| 12- Month Running Averages: | [7 empty] | 91.92% |  | 85% |  | #REF! |  | #REF! |  |  | 94.5% | 85%
NOTES:
(1) | All weighted averages based on Total Flow.
(2) | System-Wide (weighted average) limit for TSS and CBOD % Removals: 85%; and a 12-month running avg. of 85%.
(3) | Permit flows are for 12-month rolling averages of the total flows.

## May 2015
MONTHLY OPERATING EFFICIENCY
CITY-WIDE BUBBLE
May | FLOW |  |  | TOTAL SUSPENDED SOLIDS | [7 empty] | CARBONACEOUS BIOCHEMICAL OXYGEN DEMAND
2015 | (MGD) |  |  | INFL |  | EFFLUENT (mg/L) |  |  | % REMOVAL |  |  | INFL |  | EFFLUENT (mg/L) |  |  | % REMOVAL
PLANT | ACTUAL | 12-M RA | PERMIT | (mg/L) |  | ACTUAL |  | PERMIT | ACTUAL |  | PERMIT | (mg/L) |  | ACTUAL |  | PERMIT | ACTUAL |  | PERMIT
WARDS ISLAND | 203 | 209 | 275 |  | 126 |  | 10 | 30 |  | 92% | 85% |  | 97 |  | 4 | 25 |  | 96% | 85%
NORTH RIVER | 108 | 116 | 170 |  | 194 |  | 16 | 30 |  | 91% | 85% |  | 146 |  | 10 | 25 |  | 93% | 85%
HUNTS POINT | 112 | 120 | 200 |  | 136 |  | 3 | 30 |  | 98% | 85% |  | 110 |  | 2 | 25 |  | 98% | 85%
26TH WARD | 37 | 45 | 85 |  | 146 |  | 5 | 30 |  | 97% | 85% |  | 165 |  | 4 | 25 |  | 98% | 85%
CONEY ISLAND | 72 | 85 | 110 |  | 161 |  | 25 | 30 |  | 84% | 85% |  | 149 |  | 10 | 25 |  | 93% | 85%
OWLS HEAD | 85 | 93 | 120 |  | 210 |  | 14 | 30 |  | 94% | 85% |  | 194 |  | 8 | 25 |  | 96% | 85%
NEWTOWN CREEK | 194 | 218 | 310 |  | 174 |  | 13 | 30 |  | 93% | 85% |  | 186 |  | 13 | 25 |  | 93% | 85%
RED HOOK | 24 | 27 | 60 |  | 206 |  | 4 | 30 |  | 98% | 85% |  | 216 |  | 5 | 25 |  | 98% | 85%
JAMAICA | 74 | 79 | 100 |  | 159 |  | 7 | 30 |  | 96% | 85% |  | 198 |  | 5 | 25 |  | 98% | 85%
TALLMAN ISLAND | 50 | 57.9167 | 80 |  | 151 |  | 11 | 30 |  | 93% | 85% |  | 135 |  | 6 | 25 |  | 96% | 85%
BOWERY BAY | 98 | 108 | 150 |  | 175 |  | 4 | 30 |  | 98% | 85% |  | 149 |  | 3 | 25 |  | 99% | 85%
ROCKAWAY | 14 | 16 | 45 |  | 128 |  | 7 | 30 |  | 95% | 85% |  | 128 |  | 3 | 25 |  | 98% | 85%
OAKWOOD BEACH | 24.4 | 28.1 | 39.9 |  | 185 |  | 12 | 30 |  | 94% | 85% |  | 152 |  | 8 | 25 |  | 95% | 85%
PORT RICHMOND | 25 | 30 | 60 |  | 192 |  | 3 | 30 |  | 98% | 85% |  | 256 |  | 4 | 25 |  | 98% | 85%
TOTAL | 1120 | 1232 | 1804.9
Weighted Average |  |  |  |  | 163.2839 |  | 10.5471 |  |  | 94% |  |  | 152.0311 |  | 6.7921 |  |  | 96% | 85%
| 12- Month Running Averages: | [7 empty] | 92.17% |  | 85% |  | #REF! |  | #REF! |  |  | 94.67% | 85%
NOTES:
(1) | All weighted averages based on Total Flow.
(2) | System-Wide (weighted average) limit for TSS and CBOD % Removals: 85%; and a 12-month running avg. of 85%.
(3) | Permit flows are for 12-month rolling averages of the total flows.

## June 2015
MONTHLY OPERATING EFFICIENCY
CITY-WIDE BUBBLE
June | FLOW |  |  | TOTAL SUSPENDED SOLIDS | [7 empty] | CARBONACEOUS BIOCHEMICAL OXYGEN DEMAND
2015 | (MGD) |  |  | INFL |  | EFFLUENT (mg/L) |  |  | % REMOVAL |  |  | INFL |  | EFFLUENT (mg/L) |  |  | % REMOVAL
PLANT | ACTUAL | 12-M RA | PERMIT | (mg/L) |  | ACTUAL |  | PERMIT | ACTUAL |  | PERMIT | (mg/L) |  | ACTUAL |  | PERMIT | ACTUAL |  | PERMIT
WARDS ISLAND | 220 | 209 | 275 |  | 125 |  | 6 | 30 |  | 95% | 85% |  | 91 |  | 4 | 25 |  | 96% | 85%
NORTH RIVER | 117 | 116 | 170 |  | 161 |  | 27 | 30 |  | 84% | 85% |  | 130 |  | 13 | 25 |  | 91% | 85%
HUNTS POINT | 126 | 120 | 200 |  | 111 |  | 5 | 30 |  | 95% | 85% |  | 99 |  | 2 | 25 |  | 98% | 85%
26TH WARD | 50 | 45 | 85 |  | 108 |  | 6 | 30 |  | 95% | 85% |  | 136 |  | 5 | 25 |  | 96% | 85%
CONEY ISLAND | 90 | 85 | 110 |  | 252 |  | 10 | 30 |  | 97% | 85% |  | 158 |  | 4 | 25 |  | 97% | 85%
OWLS HEAD | 95 | 93 | 120 |  | 180 |  | 13 | 30 |  | 94% | 85% |  | 171 |  | 7 | 25 |  | 97% | 85%
NEWTOWN CREEK | 228 | 219 | 310 |  | 165 |  | 9 | 30 |  | 95% | 85% |  | 177 |  | 11 | 25 |  | 94% | 85%
RED HOOK | 29 | 27 | 60 |  | 175 |  | 5 | 30 |  | 97% | 85% |  | 176 |  | 6 | 25 |  | 97% | 85%
JAMAICA | 80 | 79 | 100 |  | 161 |  | 5 | 30 |  | 97% | 85% |  | 196 |  | 4 | 25 |  | 98% | 85%
TALLMAN ISLAND | 65 | 58.3333 | 80 |  | 132 |  | 10 | 30 |  | 94% | 85% |  | 101 |  | 6 | 25 |  | 94% | 85%
BOWERY BAY | 116 | 109 | 150 |  | 143 |  | 4 | 30 |  | 97% | 85% |  | 129 |  | 3 | 25 |  | 99% | 85%
ROCKAWAY | 16 | 16 | 45 |  | 117 |  | 9 | 30 |  | 92% | 85% |  | 115 |  | 6 | 25 |  | 95% | 85%
OAKWOOD BEACH | 28.3 | 27.9 | 39.9 |  | 156 |  | 8 | 30 |  | 95% | 85% |  | 147 |  | 6 | 25 |  | 96% | 85%
PORT RICHMOND | 30 | 30 | 60 |  | 184 |  | 4 | 30 |  | 98% | 85% |  | 234 |  | 3 | 25 |  | 99% | 85%
TOTAL | 1290 | 1234 | 1804.9
Weighted Average |  |  |  |  | 153.5293 |  | 9.105 |  |  | 94% |  |  | 140.045 |  | 6.22 |  |  | 96% | 85%
| 12- Month Running Averages: | [7 empty] | 92.33% |  | 85% |  | #REF! |  | #REF! |  |  | 94.75% | 85%
NOTES:
(1) | All weighted averages based on Total Flow.
(2) | System-Wide (weighted average) limit for TSS and CBOD % Removals: 85%; and a 12-month running avg. of 85%.
(3) | Permit flows are for 12-month rolling averages of the total flows.

## July 2015
MONTHLY OPERATING EFFICIENCY
CITY-WIDE BUBBLE
July | FLOW |  |  | TOTAL SUSPENDED SOLIDS | [7 empty] | CARBONACEOUS BIOCHEMICAL OXYGEN DEMAND
2015 | (MGD) |  |  | INFL |  | EFFLUENT (mg/L) |  |  | % REMOVAL |  |  | INFL |  | EFFLUENT (mg/L) |  |  | % REMOVAL
PLANT | ACTUAL | 12-M RA | PERMIT | (mg/L) |  | ACTUAL |  | PERMIT | ACTUAL |  | PERMIT | (mg/L) |  | ACTUAL |  | PERMIT | ACTUAL |  | PERMIT
WARDS ISLAND | 222 | 209 | 275 |  | 107 |  | 4 | 30 |  | 96% | 85% |  | 88 |  | 3 | 25 |  | 97% | 85%
NORTH RIVER | 112 | 115 | 170 |  | 137 |  | 19 | 30 |  | 88% | 85% |  | 125 |  | 11 | 25 |  | 92% | 85%
HUNTS POINT | 122 | 120 | 200 |  | 104 |  | 3 | 30 |  | 97% | 85% |  | 98 |  | 3 | 25 |  | 97% | 85%
26TH WARD | 43 | 44 | 85 |  | 130 |  | 4 | 30 |  | 97% | 85% |  | 145 |  | 4 | 25 |  | 97% | 85%
CONEY ISLAND | 84 | 85 | 110 |  | 200 |  | 8 | 30 |  | 97% | 85% |  | 133 |  | 5 | 25 |  | 97% | 85%
OWLS HEAD | 84 | 92 | 120 |  | 173 |  | 12 | 30 |  | 93% | 85% |  | 163 |  | 7 | 25 |  | 96% | 85%
NEWTOWN CREEK | 214 | 218 | 310 |  | 161 |  | 11 | 30 |  | 93% | 85% |  | 165 |  | 10 | 25 |  | 94% | 85%
RED HOOK | 26 | 27 | 60 |  | 158 |  | 4 | 30 |  | 97% | 85% |  | 176 |  | 5 | 25 |  | 97% | 85%
JAMAICA | 76 | 78 | 100 |  | 161 |  | 7 | 30 |  | 96% | 85% |  | 192 |  | 6 | 25 |  | 97% | 85%
TALLMAN ISLAND | 55 | 58.0833 | 80 |  | 130 |  | 7 | 30 |  | 95% | 85% |  | 114 |  | 7 | 25 |  | 94% | 85%
BOWERY BAY | 103 | 109 | 150 |  | 145 |  | 4 | 30 |  | 97% | 85% |  | 140 |  | 3 | 25 |  | 98% | 85%
ROCKAWAY | 18 | 16 | 45 |  | 111 |  | 8 | 30 |  | 93% | 85% |  | 99 |  | 4 | 25 |  | 96% | 85%
OAKWOOD BEACH | 25.5 | 27.5 | 39.9 |  | 182 |  | 5 | 30 |  | 97% | 85% |  | 138 |  | 5 | 25 |  | 96% | 85%
PORT RICHMOND | 25 | 29 | 60 |  | 197 |  | 7 | 30 |  | 96% | 85% |  | 247 |  | 5 | 25 |  | 98% | 85%
TOTAL | 1210 | 1228 | 1804.9
Weighted Average |  |  |  |  | 143.1033 |  | 7.8244 |  |  | 95% |  |  | 134.905 |  | 5.9409 |  |  | 96% | 85%
| 12- Month Running Averages: | [7 empty] | 92.42% |  | 85% |  | #REF! |  | #REF! |  |  | 94.83% | 85%
NOTES:
(1) | All weighted averages based on Total Flow.
(2) | System-Wide (weighted average) limit for TSS and CBOD % Removals: 85%; and a 12-month running avg. of 85%.
(3) | Permit flows are for 12-month rolling averages of the total flows.

## August 2015
MONTHLY OPERATING EFFICIENCY
CITY-WIDE BUBBLE
August | FLOW |  |  | TOTAL SUSPENDED SOLIDS | [7 empty] | CARBONACEOUS BIOCHEMICAL OXYGEN DEMAND
2015 | (MGD) |  |  | INFL |  | EFFLUENT (mg/L) |  |  | % REMOVAL |  |  | INFL |  | EFFLUENT (mg/L) |  |  | % REMOVAL
PLANT | ACTUAL | 12-M RA | PERMIT | (mg/L) |  | ACTUAL |  | PERMIT | ACTUAL |  | PERMIT | (mg/L) |  | ACTUAL |  | PERMIT | ACTUAL |  | PERMIT
WARDS ISLAND | 212 | 208 | 275 |  | 109 |  | 4 | 30 |  | 96% | 85% |  | 85 |  | 3 | 25 |  | 96% | 85%
NORTH RIVER | 115 | 115 | 170 |  | 140 |  | 10 | 30 |  | 93% | 85% |  | 120 |  | 7 | 25 |  | 94% | 85%
HUNTS POINT | 122 | 122 | 200 |  | 102 |  | 3 | 30 |  | 97% | 85% |  | 98 |  | 1 | 25 |  | 99% | 85%
26TH WARD | 43 | 44 | 85 |  | 93 |  | 3 | 30 |  | 97% | 85% |  | 126 |  | 3 | 25 |  | 98% | 85%
CONEY ISLAND | 83 | 85 | 110 |  | 321 |  | 23 | 30 |  | 94% | 85% |  | 166 |  | 8 | 25 |  | 96% | 85%
OWLS HEAD | 81 | 92 | 120 |  | 161 |  | 12 | 30 |  | 93% | 85% |  | 169 |  | 7 | 25 |  | 96% | 85%
NEWTOWN CREEK | 209 | 216 | 310 |  | 164 |  | 8 | 30 |  | 95% | 85% |  | 153 |  | 8 | 25 |  | 95% | 85%
RED HOOK | 25 | 27 | 60 |  | 163 |  | 4 | 30 |  | 98% | 85% |  | 167 |  | 4 | 25 |  | 98% | 85%
JAMAICA | 75 | 78 | 100 |  | 151 |  | 5 | 30 |  | 97% | 85% |  | 177 |  | 4 | 25 |  | 98% | 85%
TALLMAN ISLAND | 56 | 58.1667 | 80 |  | 126 |  | 8 | 30 |  | 94% | 85% |  | 108 |  | 5 | 25 |  | 95% | 85%
BOWERY BAY | 100 | 108 | 150 |  | 133 |  | 5 | 30 |  | 96% | 85% |  | 136 |  | 3 | 25 |  | 98% | 85%
ROCKAWAY | 18 | 16 | 45 |  | 100 |  | 6 | 30 |  | 94% | 85% |  | 99 |  | 4 | 25 |  | 96% | 85%
OAKWOOD BEACH | 23.6 | 27.4 | 39.9 |  | 233 |  | 5 | 30 |  | 98% | 85% |  | 169 |  | 6 | 25 |  | 96% | 85%
PORT RICHMOND | 23 | 28 | 60 |  | 208 |  | 4 | 30 |  | 98% | 85% |  | 280 |  | 4 | 25 |  | 99% | 85%
TOTAL | 1186 | 1225 | 1804.9
Weighted Average |  |  |  |  | 150 |  | 7 |  |  | 95% |  |  | 133 |  | 5 |  |  | 96% | 85%
| 12- Month Running Averages: | [7 empty] | 92.42% |  | 85% |  | #REF! |  | #REF! |  |  | 94.83% | 85%
NOTES:
(1) | All weighted averages based on Total Flow.
(2) | System-Wide (weighted average) limit for TSS and CBOD % Removals: 85%; and a 12-month running avg. of 85%.
(3) | Permit flows are for 12-month rolling averages of the total flows.

## September 2015
MONTHLY OPERATING EFFICIENCY
CITY-WIDE BUBBLE
September | FLOW |  |  | TOTAL SUSPENDED SOLIDS | [7 empty] | CARBONACEOUS BIOCHEMICAL OXYGEN DEMAND
2015 | (MGD) |  |  | INFL |  | EFFLUENT (mg/L) |  |  | % REMOVAL |  |  | INFL |  | EFFLUENT (mg/L) |  |  | % REMOVAL
PLANT | ACTUAL | 12-M RA | PERMIT | (mg/L) |  | ACTUAL |  | PERMIT | ACTUAL |  | PERMIT | (mg/L) |  | ACTUAL |  | PERMIT | ACTUAL |  | PERMIT
WARDS ISLAND | 205 | 208 | 275 |  | 120 |  | 4 | 30 |  | 97% | 85% |  | 98 |  | 3 | 25 |  | 97% | 85%
NORTH RIVER | 117 | 116 | 170 |  | 164 |  | 10 | 30 |  | 95% | 85% |  | 133 |  | 7 | 25 |  | 95% | 85%
HUNTS POINT | 119 | 124 | 200 |  | 113 |  | 4 | 30 |  | 96% | 85% |  | 112 |  | 2 | 25 |  | 98% | 85%
26TH WARD | 42 | 44 | 85 |  | 120 |  | 4 | 30 |  | 97% | 85% |  | 145 |  | 4 | 25 |  | 97% | 85%
CONEY ISLAND | 92 | 86 | 110 |  | 247 |  | 7 | 30 |  | 98% | 85% |  | 143 |  | 4 | 25 |  | 97% | 85%
OWLS HEAD | 91 | 92 | 120 |  | 156 |  | 23 | 30 |  | 84% | 85% |  | 166 |  | 12 | 25 |  | 93% | 85%
NEWTOWN CREEK | 216 | 218 | 310 |  | 163 |  | 10 | 30 |  | 94% | 85% |  | 160 |  | 9 | 25 |  | 94% | 85%
RED HOOK | 26 | 27 | 60 |  | 193 |  | 3 | 30 |  | 98% | 85% |  | 187 |  | 5 | 25 |  | 97% | 85%
JAMAICA | 76 | 79 | 100 |  | 160 |  | 5 | 30 |  | 97% | 85% |  | 191 |  | 4 | 25 |  | 98% | 85%
TALLMAN ISLAND | 55 | 58.25 | 80 |  | 140 |  | 8 | 30 |  | 94% | 85% |  | 132 |  | 6 | 25 |  | 95% | 85%
BOWERY BAY | 104 | 109 | 150 |  | 148 |  | 4 | 30 |  | 97% | 85% |  | 144 |  | 3 | 25 |  | 98% | 85%
ROCKAWAY | 18 | 16 | 45 |  | 97 |  | 5 | 30 |  | 95% | 85% |  | 96 |  | 3 | 25 |  | 97% | 85%
OAKWOOD BEACH | 24.2 | 27.4 | 39.9 |  | 184 |  | 4 | 30 |  | 98% | 85% |  | 151 |  | 6 | 25 |  | 96% | 85%
PORT RICHMOND | 25 | 29 | 60 |  | 254 |  | 5 | 30 |  | 98% | 85% |  | 292 |  | 5 | 25 |  | 98% | 85%
TOTAL | 1210 | 1234 | 1804.9
Weighted Average |  |  |  |  | 154.7288 |  | 7.5676 |  |  | 95% |  |  | 142 |  | 5 |  |  | 96% | 85%
| 12- Month Running Averages: | [7 empty] | 93% |  | 85% |  | #REF! |  | #REF! |  |  | 94.83% | 85%
NOTES:
(1) | All weighted averages based on Total Flow.
(2) | System-Wide (weighted average) limit for TSS and CBOD % Removals: 85%; and a 12-month running avg. of 85%.
(3) | Permit flows are for 12-month rolling averages of the total flows.

## October 2015
MONTHLY OPERATING EFFICIENCY
CITY-WIDE BUBBLE
October | FLOW |  |  | TOTAL SUSPENDED SOLIDS | [7 empty] | CARBONACEOUS BIOCHEMICAL OXYGEN DEMAND
2015 | (MGD) |  |  | INFL |  | EFFLUENT (mg/L) |  |  | % REMOVAL |  |  | INFL |  | EFFLUENT (mg/L) |  |  | % REMOVAL
PLANT | ACTUAL | 12-M RA | PERMIT | (mg/L) |  | ACTUAL |  | PERMIT | ACTUAL |  | PERMIT | (mg/L) |  | ACTUAL |  | PERMIT | ACTUAL |  | PERMIT
WARDS ISLAND | 202 | 208 | 275 |  | 123 |  | 6 | 30 |  | 97% | 85% |  | 105 |  | 3 | 25 |  | 97% | 85%
NORTH RIVER | 117 | 115 | 170 |  | 164 |  | 9 | 30 |  | 95% | 85% |  | 147 |  | 6 | 25 |  | 97% | 85%
HUNTS POINT | 125 | 125 | 200 |  | 112 |  | 4 | 30 |  | 97% | 85% |  | 107 |  | 3 | 25 |  | 98% | 85%
26TH WARD | 44 | 44 | 85 |  | 108 |  | 5 | 30 |  | 96% | 85% |  | 145 |  | 4 | 25 |  | 97% | 85%
CONEY ISLAND | 93 | 87 | 110 |  | 181 |  | 10 | 30 |  | 96% | 85% |  | 163 |  | 8 | 25 |  | 96% | 85%
OWLS HEAD | 97 | 92 | 120 |  | 177 |  | 25 | 30 |  | 88% | 85% |  | 192 |  | 12 | 25 |  | 94% | 85%
NEWTOWN CREEK | 220 | 218 | 310 |  | 163 |  | 11 | 30 |  | 94% | 85% |  | 167 |  | 13 | 25 |  | 92% | 85%
RED HOOK | 27 | 27 | 60 |  | 187 |  | 5 | 30 |  | 97% | 85% |  | 188 |  | 5 | 25 |  | 97% | 85%
JAMAICA | 77 | 79 | 100 |  | 151 |  | 5 | 30 |  | 97% | 85% |  | 194 |  | 5 | 25 |  | 97% | 85%
TALLMAN ISLAND | 57 | 58.1667 | 80 |  | 131 |  | 7 | 30 |  | 95% | 85% |  | 134 |  | 5 | 25 |  | 96% | 85%
BOWERY BAY | 105 | 108 | 150 |  | 143 |  | 5 | 30 |  | 97% | 85% |  | 136 |  | 3 | 25 |  | 98% | 85%
ROCKAWAY | 18 | 16 | 45 |  | 84 |  | 5 | 30 |  | 94% | 85% |  | 114 |  | 4 | 25 |  | 96% | 85%
OAKWOOD BEACH | 26.1 | 27.4 | 39.9 |  | 145 |  | 4 | 30 |  | 97% | 85% |  | 156 |  | 9 | 25 |  | 94% | 85%
PORT RICHMOND | 26 | 29 | 60 |  | 204 |  | 10 | 30 |  | 95% | 85% |  | 375 |  | 11 | 25 |  | 97% | 85%
TOTAL | 1234 | 1234 | 1804.9
Weighted Average |  |  |  |  | 147.8173 |  | 8.6373 |  |  | 94% |  |  | 151.1285 |  | 6.7584 |  |  | 96% | 85%
| 12- Month Running Averages: | [7 empty] | 92.75% |  | 85% |  | #REF! |  | #REF! |  |  | 95% | 85%
NOTES:
(1) | All weighted averages based on Total Flow.
(2) | System-Wide (weighted average) limit for TSS and CBOD % Removals: 85%; and a 12-month running avg. of 85%.
(3) | Permit flows are for 12-month rolling averages of the total flows.

## November 2015
MONTHLY OPERATING EFFICIENCY
CITY-WIDE BUBBLE
November | FLOW |  |  | TOTAL SUSPENDED SOLIDS | [7 empty] | CARBONACEOUS BIOCHEMICAL OXYGEN DEMAND
2015 | (MGD) |  |  | INFL |  | EFFLUENT (mg/L) |  |  | % REMOVAL |  |  | INFL |  | EFFLUENT (mg/L) |  |  | % REMOVAL
PLANT | ACTUAL | 12-M RA | PERMIT | (mg/L) |  | ACTUAL |  | PERMIT | ACTUAL |  | PERMIT | (mg/L) |  | ACTUAL |  | PERMIT | ACTUAL |  | PERMIT
WARDS ISLAND | 187 | 207 | 275 |  | 128 |  | 4 | 30 |  | 97% | 85% |  | 115 |  | 3 | 25 |  | 97% | 85%
NORTH RIVER | 108 | 115 | 170 |  | 150 |  | 8 | 30 |  | 95% | 85% |  | 146 |  | 6 | 25 |  | 96% | 85%
HUNTS POINT | 123 | 125 | 200 |  | 121 |  | 5 | 30 |  | 96% | 85% |  | 113 |  | 2 | 25 |  | 98% | 85%
26TH WARD | 39 | 43 | 85 |  | 112 |  | 4 | 30 |  | 96% | 85% |  | 158 |  | 4 | 25 |  | 97% | 85%
CONEY ISLAND | 80 | 86 | 110 |  | 223 |  | 8 | 30 |  | 97% | 85% |  | 194 |  | 6 | 25 |  | 97% | 85%
OWLS HEAD | 101 | 93 | 120 |  | 165 |  | 53 | 30 |  | 72% | 85% |  | 198 |  | 22 | 25 |  | 91% | 85%
NEWTOWN CREEK | 202 | 216 | 310 |  | 159 |  | 9 | 30 |  | 94% | 85% |  | 162 |  | 11 | 25 |  | 93% | 85%
RED HOOK | 25 | 27 | 60 |  | 193 |  | 4 | 30 |  | 98% | 85% |  | 199 |  | 5 | 25 |  | 97% | 85%
JAMAICA | 71 | 79 | 100 |  | 144 |  | 5 | 30 |  | 97% | 85% |  | 192 |  | 5 | 25 |  | 97% | 85%
TALLMAN ISLAND | 51 | 57.5 | 80 |  | 150 |  | 25 | 30 |  | 84% | 85% |  | 143 |  | 8 | 25 |  | 94% | 85%
BOWERY BAY | 98 | 107 | 150 |  | 145 |  | 4 | 30 |  | 97% | 85% |  | 153 |  | 2 | 25 |  | 99% | 85%
ROCKAWAY | 16 | 16 | 45 |  | 102 |  | 6 | 30 |  | 94% | 85% |  | 122 |  | 4 | 25 |  | 97% | 85%
OAKWOOD BEACH | 23.7 | 27.2 | 39.9 |  | 179 |  | 5 | 30 |  | 97% | 85% |  | 176 |  | 7 | 25 |  | 96% | 85%
PORT RICHMOND | 25 | 28 | 60 |  | 220 |  | 18 | 30 |  | 92% | 85% |  | 367 |  | 13 | 25 |  | 96% | 85%
TOTAL | 1150 | 1227 | 1804.9
Weighted Average |  |  |  |  | 151.5594 |  | 11.2874 |  |  | 93% |  |  | 158.0593 |  | 7.1077 |  |  | 96% | 85%
| 12- Month Running Averages: | [7 empty] | 92.75% |  | 85% |  | #REF! |  | #REF! |  |  | 95% | 85%
NOTES:
(1) | All weighted averages based on Total Flow.
(2) | System-Wide (weighted average) limit for TSS and CBOD % Removals: 85%; and a 12-month running avg. of 85%.
(3) | Permit flows are for 12-month rolling averages of the total flows.

## December 2015
c2..p38
M:\OpenData\Data to upload\Uploaded (Week of 8.19.16)\DEP\[Monthly_Operating_Efficiency.xlsx]December 2015 | MONTHLY OPERATING EFFICIENCY
16 | CITY-WIDE BUBBLE | [19 empty] | December | 2015
)\
For Mayor's Management
| December | FLOW |  |  | TOTAL SUSPENDED SOLIDS | [7 empty] | CARBONACEOUS BIOCHEMICAL OXYGEN DEMAND
| 2015 | (MGD) |  |  | INFL |  | EFFLUENT (mg/L) |  |  | % REMOVAL |  |  | INFL |  | EFFLUENT (mg/L) |  |  | % REMOVAL |  |  | MILLION GALLONS BYPASSED
| PLANT | ACTUAL | 12-M RA | PERMIT | (mg/L) |  | ACTUAL |  | PERMIT | ACTUAL |  | PERMIT | (mg/L) |  | ACTUAL |  | PERMIT | ACTUAL |  | PERMIT | DAYS THIS MONTH |  | #N/A
| WARDS ISLAND | 198 | 206 | 275 |  | 117 |  | 7 | 30 |  | 94% | 85% |  | 107 |  | 3 | 25 |  | 97% | 85% | PERCENT OF SEWAGE NOT TREATED |  | #REF!
| NORTH RIVER | 114 | 114 | 170 |  | 150 |  | 13 | 30 |  | 91% | 85% |  | 148 |  | 8 | 25 |  | 95% | 85%
| HUNTS POINT | 124 | 124 | 200 |  | 109 |  | 9 | 30 |  | 94% | 85% |  | 106 |  | 3 | 25 |  | 97% | 85%
| 26TH WARD | 45 | 43 | 85 |  | 100 |  | 5 | 30 |  | 96% | 85% |  | 132 |  | 4 | 25 |  | 97% | 85%
| CONEY ISLAND | 87 | 86 | 110 |  | 175 |  | 7 | 30 |  | 97% | 85% |  | 175 |  | 6 | 25 |  | 97% | 85%
| OWLS HEAD | 96 | 93 | 120 |  | 178 |  | 28 | 30 |  | 85% | 85% |  | 203 |  | 14 | 25 |  | 94% | 85%
| NEWTOWN CREEK | 211 | 215 | 310 |  | 161 |  | 10 | 30 |  | 94% | 85% |  | 168 |  | 11 | 25 |  | 94% | 85%
| RED HOOK | 26 | 26 | 60 |  | 189 |  | 5 | 30 |  | 97% | 85% |  | 190 |  | 5 | 25 |  | 97% | 85%
| JAMAICA | 74 | 78 | 100 |  | 151 |  | 13 | 30 |  | 91% | 85% |  | 186 |  | 9 | 25 |  | 95% | 85%
| TALLMAN ISLAND | 58 | 56.9167 | 80 |  | 130 |  | 9 | 30 |  | 95% | 85% |  | 137 |  | 5 | 25 |  | 97% | 85%
| BOWERY BAY | 105 | 106 | 150 |  | 130 |  | 8 | 30 |  | 95% | 85% |  | 139 |  | 4 | 25 |  | 97% | 85%
| ROCKAWAY | 15 | 16 | 45 |  | 94 |  | 5 | 30 |  | 95% | 85% |  | 126 |  | 3 | 25 |  | 98% | 85%
| OAKWOOD BEACH | 25.4 | 26.7 | 39.9 |  | 189 |  | 6 | 30 |  | 97% | 85% |  | 180 |  | 7 | 25 |  | 96% | 85%
| PORT RICHMOND | 27 | 28 | 60 |  | 231 |  | 15 | 30 |  | 94% | 85% |  | 391 |  | 12 | 25 |  | 97% | 85%
| TOTAL | 1205 | 1219 | 1804.9
| Weighted Average |  |  |  |  | 144.6403 |  | 10.5414 |  |  | 93% |  |  | 153.9975 |  | 6.8861 |  |  | 96% | 85%
|  | 12- Month Running Averages: | [7 empty] | 92.92% |  | 85% |  | #REF! |  | #REF! |  |  | 95.17% | 85%
NOTES:
| (1) | All weighted averages based on Total Flow.
| (2) | System-Wide (weighted average) limit for TSS and CBOD % Removals: 85%; and a 12-month running avg. of 85%.
| (3) | Permit flows are for 12-month rolling averages of the total flows.
|  | STEP AERATION PLANTS | [9 empty] | REMEMBER TO UPDATE PERCENT REMOVALS ON OTHER TAB!
|  | DRY |  | AVG. |  | AVG.
|  | FLOW | FLOW | EFF. SS |  | EFF. CBOD
|  | (BGD) | (BGD) | (mg/L) |  | (mg/L)
|  | 1.205 | 1.219 | 10.5414 |  | 6.8861
updated values
reviewed
196
233
274
289
302
304
300
299
300
296
284
281
281
281
276
272
274
265
241
226
211
197
189
188
260.7917